{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":37,"n_cols":11,"rows_kept":37,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["American Wire Gauge -- IEC 60228 Wire Size"]
[]
["AWG / kcmil","Area   Circ Mils","Amps   TW/UF (60C)","Amps THHW (75C)","Amps THHN (90C)","IEC mm2",null,"IEC mm2","Area   Circ Mils","Amps Free Air, 70C PVC","Amps    in wall, 70C PVC"]
[18,1620,"--","--",null,0.823,null,0.5,987,"  --","  --"]
[16,2580,"--","--",null,1.31,null,0.75,1480,"--","--"]
["14*",4110,"20 (15)","20 (15)","25 (20)",2.08,null,1.5,2960,17.5,13]
["12*",6530,"25 (20)","25 (20)","30 (20)",3.31,null,2.5,4934,24,17.5]
["10*",10380,30,"35 (30)","40 (30)",5.27,null,4,7894,32,23]
[8,16510,40,50,55,8.35,null,6,11841,41,29]
[6,26240,55,65,75,13.3,null,10,19735,57,39]
[4,41740,70,85,95,21.2,null,16,31576,76,52]
[3,52620,85,100,110,26.7,null,25,49338,96,68]
[2,66360,95,115,130,33.6,null,35,69073,119,83]
[1,83690,110,130,150,42.4,null,50,98676,144,99]
["1/0",105600,125,150,170,53.5,null,70,138147,184,125]
["2/0",133100,145,175,195,67.4,null,95,187485,223,150]
["3/0",167800,165,200,225,85,null,120,236823,259,172]
["4/0",211600,195,230,260,107.2,null,150,296029,299,196]
["250",250000,215,255,290,126.7,null,185,365102,341,223]
["300",300000,240,285,320,152,null,240,473646,403,261]
["350",350000,260,310,350,177.3,null,300,592058,464,298]
["400",400000,280,335,380,202.7]
["500",500000,320,380,430,253.4,null,"(table A.52.4 of IEC 60364-5-52)"]
["600",600000,355,420,475,304,null,"Fig. G20, http://tinyurl.com/2u3pzqd"]
["700",700000,385,460,520]
["750",750000,400,475,535]
["800",800000,410,490,555]
["900",900000,435,520,585]
["1000",1000000,455,545,615]
[]
["   * Maximum overcurrent protection for # 14 = 15A, # 12 = 20A, # 10 = 30A"]
[]
["NEC 2007, Chap 9, Table 8, via Ugly's Electrical Ref 2008, pp71, 73"]
[]
[]
["mm2 - Circ Mils equivalance via "]
["http://www.mogami.com/e/cad/wire-gauge.html"]