{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["GMC-9~85(AC operatingcontactor)","GMD-9~85(DC operating contactor","GMC100~GMC800"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"GMC-9~85(AC operatingcontactor)","index":0,"n_rows":80,"n_cols":22,"rows_kept":80,"cut":false,"hidden":false,"merged":[[44,6,80,6],[44,7,80,7],[44,14,80,14],[42,12,42,13],[42,14,43,14],[1,0,2,0],[3,6,39,6],[3,7,39,7],[1,14,2,14],[1,1,2,1],[1,8,1,9],[1,10,1,11],[3,14,39,14],[1,12,1,13],[42,0,43,0],[42,1,43,1],[42,8,42,9],[42,10,42,11]],"flags":["formulas_cached_only"]}
[" CHARACTERISTICS OF GMC-9~40 COILS"]
["Frame","Rating Voltage","Inrush Current (A)",null,"Holding Current (A)",null,"Closing ","Opening","Consumption(W)",null,"Pick-up Voltage",null,"Drop-out Voltage",null,"Remark"]
[null,null,"AC50HZ","AC60HZ","AC50HZ","AC60HZ","time (ms)","time (ms)","AC50HZ","AC60HZ","AC50HZ","AC60HZ","AC50HZ","AC60HZ"]
["GMC-9~40",24,3.154,2.945,0.45,0.354,"20ms↓","15ms↓",2.9,2.3,16.3,18.7,12,14]
["   (50/60Hz)",48,1.577,1.472,0.225,0.177,null,null,2.9,2.3,33,39,22,24]
[null,110,0.688,0.642,0.098,0.077,null,null,2.9,2.3,76,85,50,61]
[null,220,0.344,0.321,0.049,0.038,null,null,2.9,2.3,150,172,100,120]
[null,240,0.315,0.294,0.045,0.035,null,null,2.9,2.3,162,186,130,150]
[null,380,0.199,0.186,0.028,0.022,null,null,2.9,2.3,260,300,190,220]
[null,400,0.189,0.176,0.027,0.021,null,null,2.9,2.3,270,310,210,230]
[null,415,0.182,0.17,0.026,0.02,null,null,2.9,2.3,290,315,230,250]
[null,440,0.172,0.16,0.024,0.019,null,null,2.9,2.3,300,335,240,270]
[null,500,0.151,0.141,0.021,0.017,null,null,2.9,2.3,340,400,270,300]
[null,550,0.137,0.128,0.019,0.015,null,null,2.9,2.3,370,440,290,320]
["GMC-9~40",24,"-",2.945,"-",0.45,null,null,"-",2.3,"-",18.4,"-",12]
["   (60Hz)",48,"-",1.472,"-",0.225,null,null,"-",2.3,"-",36,"-",24]
[null,110,"-",0.642,"-",0.098,null,null,"-",2.3,"-",82,"-",55]
[null,120,"-",0.589,"-",0.09,null,null,"-",2.3,"-",90,"-",62]
[null,208,"-",0.339,"-",0.051,null,null,"-",2.3,"-",150,"-",120]
[null,220,"-",0.321,"-",0.049,null,null,"-",2.3,"-",161,"-",100]
[null,240,"-",0.294,"-",0.045,null,null,"-",2.3,"-",171,"-",115]
[null,277,"-",0.255,"-",0.038,null,null,"-",2.3,"-",200,"-",155]
[null,380,"-",0.186,"-",0.028,null,null,"-",2.3,"-",280,"-",210]
[null,440,"-",0.16,"-",0.024,null,null,"-",2.3,"-",320,"-",240]
[null,480,"-",0.147,"-",0.022,null,null,"-",2.3,"-",365,"-",260]
[null,600,"-",0.117,"-",0.018,null,null,"-",2.3,"-",435,"-",280]
["GMC-9~40",24,3.154,"-",0.354,"-",null,null,2.9,"-",17.2,"-",12,"-"]
["   (50Hz)",42,1.802,"-",0.202,"-",null,null,2.9,"-",30,"-",20,"-"]
[null,48,1.577,"-",0.177,"-",null,null,2.9,"-",33,"-",22,"-"]
[null,100,0.757,"-",0.085,"-",null,null,2.9,"-",70,"-",45,"-"]
[null,110,0.688,"-",0.077,"-",null,null,2.9,"-",82,"-",50,"-"]
[null,220,0.344,"-",0.038,"-",null,null,2.9,"-",155,"-",110,"-"]
[null,240,0.315,"-",0.035,"-",null,null,2.9,"-",175,"-",120,"-"]
[null,380,0.199,"-",0.022,"-",null,null,2.9,"-",270,"-",200,"-"]
[null,400,0.189,"-",0.021,"-",null,null,2.9,"-",275,"-",210,"-"]
[null,415,0.182,"-",0.02,"-",null,null,2.9,"-",295,"-",235,"-"]
[null,440,0.172,"-",0.019,"-",null,null,2.9,"-",320,"-",230,"-"]
[null,500,0.151,"-",0.017,"-",null,null,2.9,"-",380,"-",270,"-"]
[null,550,0.137,"-",0.015,"-",null,null,2.9,"-",390,"-",300,"-"]
[]
[]
[" CHARACTERISTICS OF GMC-50~85 COILS"]
["Frame","Rating Voltage","Inrush Current (A)",null,"Holding Current (A)",null,"Closing ","Opening","Consumption(W)",null,"Pick-up Voltage",null,"Drop-out Voltage",null,"Remark"]
[null,null,"AC50HZ","AC60HZ","AC50HZ","AC60HZ","time (ms)","time (ms)","AC50HZ","AC60HZ","AC50HZ","AC60HZ","AC50HZ","AC60HZ"]
["GMC-50~85",24,10.283,9.87,0.616,0.5,"30ms↓","20ms↓",6.5,6.5,17,19.5,12,14,null,null,null,50,60,50,60]
["   (50/60Hz)",48,5.141,4.935,0.308,0.25,null,null,6.5,6.5,34,39,23,28,null,null,24,10.283333333333333,9.870833333333334,0.6166666666666667,0.7708333333333334,0.77]
[null,110,2.243,2.153,0.134,0.109,null,null,6.5,6.5,77,89,53,63,null,null,48,5.141666666666667,null,0.30833333333333335,0.3854166666666667,0.385]
[null,220,1.121,1.076,0.067,0.054,null,null,6.5,6.5,155,180,105,125,null,null,110,2.2436363636363637,null,0.13454545454545455,0.16818181818181818,0.168]
[null,240,1.028,0.987,0.061,0.05,null,null,6.5,6.5,168,194,110,140,null,null,120,2.0566666666666666,null,0.12333333333333334,0.15416666666666667,0.154]
[null,380,0.649,0.623,0.038,0.031,null,null,6.5,6.5,265,310,185,220,null,null,208,1.1865384615384615,null,0.07115384615384615,0.0889423076923077,0.088]
[null,400,0.617,0.592,0.037,0.03,null,null,6.5,6.5,275,325,200,240,null,null,220,1.1218181818181818,null,0.06727272727272728,0.08409090909090909,0.084]
[null,415,0.594,0.57,0.035,0.028,null,null,6.5,6.5,290,340,200,250,null,null,240,1.0283333333333333,null,0.06166666666666667,0.07708333333333334,0.077]
[null,440,0.56,0.538,0.033,0.027,null,null,6.5,6.5,305,358,248,250,null,null,277,0.8909747292418773,null,0.053429602888086646,0.06678700361010831,0.066]
[null,500,0.493,0.473,0.029,0.024,null,null,6.5,6.5,345,408,250,290,null,null,380,0.6494736842105263,null,0.03894736842105263,0.04868421052631579,0.048]
[null,550,0.448,0.43,0.026,0.021,null,null,6.5,6.5,385,445,260,320,null,null,440,0.5609090909090909,null,0.03363636363636364,0.043,0.043]
["GMC-50~85",24,"-",9.87,"-",0.77,null,null,"-",6.5,"-",18,"-",12,null,null,480,0.5141666666666667,null,0.030833333333333334,0.041,0.041]
["   (60Hz)",48,"-",4.935,"-",0.385,null,null,"-",6.5,"-",36,"-",25,null,null,600,0.41133333333333333,null,0.024666666666666667,0.033,0.033]
[null,110,"-",2.153,"-",0.168,null,null,"-",6.5,"-",88,"-",40,null,null,550,0.44872727272727275,null,0.02690909090909091]
[null,120,"-",1.974,"-",0.154,null,null,"-",6.5,"-",94,"-",45]
[null,208,"-",1.138,"-",0.088,null,null,"-",6.5,"-",155,"-",100,null,null,"60Hz",236.8807716974934,12,19]
[null,220,"-",1.076,"-",0.084,null,null,"-",6.5,"-",172,"-",120,null,null,"50Hz",246.78026663410506,14.8]
[null,240,"-",0.987,"-",0.077,null,null,"-",6.5,"-",190,"-",135]
[null,277,"-",0.855,"-",0.066,null,null,"-",6.5,"-",212,"-",150]
[null,380,"-",0.623,"-",0.048,null,null,"-",6.5,"-",300,"-",210]
[null,440,"-",0.538,"-",0.043,null,null,"-",6.5,"-",340,"-",250]
[null,480,"-",0.493,"-",0.041,null,null,"-",6.5,"-",370,"-",250,{"$nulls":6},18.04]
[null,600,"-",0.394,"-",0.033,null,null,"-",6.5,"-",450,"-",320,{"$nulls":6},18.72]
["GMC-50~85",24,10.283,"-",0.616,"-",null,null,6.5,"-",18.5,"-",11,"-"]
["   (50Hz)",42,5.876,"-",0.352,"-",null,null,6.5,"-",31,"-",24,"-",{"$nulls":6},13.86]
[null,48,5.141,"-",0.308,"-",null,null,6.5,"-",37,"-",30,"-",{"$nulls":6},14.399999999999999]
[null,100,2.468,"-",0.148,"-",null,null,6.5,"-",75,"-",55,"-"]
[null,110,2.243,"-",0.134,"-",null,null,6.5,"-",85,"-",60,"-"]
[null,220,1.121,"-",0.067,"-",null,null,6.5,"-",175,"-",130,"-"]
[null,240,1.028,"-",0.061,"-",null,null,6.5,"-",185,"-",140,"-"]
[null,380,0.649,"-",0.038,"-",null,null,6.5,"-",290,"-",200,"-"]
[null,400,0.617,"-",0.037,"-",null,null,6.5,"-",300,"-",280,"-"]
[null,415,0.594,"-",0.035,"-",null,null,6.5,"-",310,"-",220,"-"]
[null,440,0.56,"-",0.033,"-",null,null,6.5,"-",325,"-",240,"-"]
[null,500,0.493,"-",0.029,"-",null,null,6.5,"-",370,"-",260,"-"]
[null,550,0.448,"-",0.026,"-",null,null,6.5,"-",410,"-",300,"-"]

{"sheet":"GMD-9~85(DC operating contactor","index":1,"n_rows":26,"n_cols":9,"rows_kept":26,"cut":false,"hidden":false,"merged":[[1,8,2,8],[3,8,12,8],[15,1,16,1],[15,8,16,8],[17,6,26,6],[17,7,26,7],[17,8,26,8],[15,0,16,0],[1,0,2,0],[3,6,12,6],[3,7,12,7],[1,1,2,1]],"flags":["formulas_cached_only"]}
[" CHARACTERISTICS OF GMD-9~40 COILS"]
["Frame","Rating Voltage","Inrush  ","Holding ","Pick-up ","Drop-out ","Closing ","Opening","Remark"]
[null,null,"Current(A)","Current (A)","Voltage","Voltage","time (ms)","time (ms)"]
["GMD9~40",12,0.758,0.758,7.2,3,"60ms↓","30ms↓"]
[null,24,0.379,0.379,15.5,7.5]
[null,48,0.189,0.189,34,9]
[null,100,0.091,0.091,72,20]
[null,110,0.082,0.082,76,25]
[null,125,0.072,0.072,81,35]
[null,200,0.045,0.045,140,60]
[null,220,0.041,0.041,145,65]
[null,250,0.036,0.036,170,80]
[]
[]
[" CHARACTERISTICS OF GMD-50~85 COILS"]
["Frame","Rating Voltage","Inrush  ","Holding ","Pick-up ","Drop-out ","Closing ","Opening","Remark"]
[null,null,"Current(A)","Current (A)","Voltage","Voltage","time (ms)","time (ms)"]
["GMD-50~85",12,36.666666666666664,0.5,9,2,"60ms↓","30ms↓"]
[null,24,18.333333333333332,0.25,17,4]
[null,48,9.166666666666666,0.125,30,6]
[null,100,4.4,0.06,56,15]
[null,110,4,0.05454545454545454,62,16]
[null,125,3.52,0.048,70,18]
[null,200,2.2,0.03,100,25]
[null,220,2,0.02727272727272727,110,27]
[null,250,1.76,0.024,135,40]

{"sheet":"GMC100~GMC800","index":2,"n_rows":44,"n_cols":11,"rows_kept":44,"cut":false,"hidden":false,"merged":[[2,6,3,6],[2,7,3,7]],"flags":["formulas_cached_only"]}
["GMC 100~800 COIL TOTAL ASS'Y Test"]
[{"$nulls":10},"'02 . 12 . 17"]
[{"$nulls":6},"Pick up","Drop out","Real Test Result"]
["Frame",null,"AC/DC","Hz","Voltage",null,null,null,"Pick up","Drop Out","Remark"]
[{"$nulls":4},"min","max","Under 80%","(30~60%)","Under 80%","(30~60%)"]
["GMC100AF","24V","AC","50Hz",{"$nulls":4},17.5,12]
["GMC125AF",null,null,"60Hz",24,25,19.2,"7.2~14.4",17.7,11.7]
["GMC150AF",null,"DC",{"$nulls":5},18,11]
[null,"48V","AC","50Hz",{"$nulls":4},36.2,22.8]
[null,null,null,"60Hz",48,50,38.4,"14.4~28.8",36.7,22.4]
[null,null,"DC",{"$nulls":5},36.3,21.8]
[null,"FV","AC","50Hz",{"$nulls":4},77.3,54.3]
[null,null,null,"60Hz",100,240,80,"30~60",77.1,53]
[null,null,"DC",{"$nulls":5},78.2,45.2]
[null,"300V","AC","60Hz",265,347,212,"80~159",200,143]
[null,"400V","AC","60Hz",380,450,304,"114~228",280,196]
[null,"500V","AC","60Hz",440,575,352,"132~264",343,236]
["GMC180AF","24V","AC","50Hz",{"$nulls":4},"17.5~18.5",11.8]
["GMC220AF",null,null,"60Hz",24,25,19.2,"7.2~14.4",17.5,11.5]
[null,null,"DC",{"$nulls":5},17.6,11]
[null,"48V","AC","50Hz",{"$nulls":4},36,22.5]
[null,null,null,"60Hz",48,50,38.4,"14.4~28.8",36,22.6]
[null,null,"DC",{"$nulls":5},36.5,20.5]
[null,"FV","AC","50Hz",{"$nulls":4},77.4,55]
[null,null,null,"60Hz",100,240,80,"30~60",77.4,53.5]
[null,null,"DC",{"$nulls":5},78.7,45.5]
[null,"300V","AC","60Hz",265,347,212,"80~159",198,149]
[null,"400V","AC","60Hz",380,450,304,"114~228",279,186]
[null,"500V","AC","60Hz",440,575,352,"132~264",344,238]
["GMC300AF","FV","AC","50Hz",{"$nulls":4},78,53.3]
["GMC400AF",null,null,"60Hz",100,240,80,"30~60",78,52]
[null,null,"DC",{"$nulls":5},79,44]
[null,"300V","AC","60Hz",265,347,212,"80~159",198,146]
[null,"400V","AC","60Hz",380,450,304,"114~228",280,190]
[null,"500V","AC","60Hz",440,575,352,"132~264",350,245]
["GMC600AF","100V","AC","50Hz",{"$nulls":4},75,51]
["GMC800AF",null,null,"60Hz",100,125,80,"30~60",74,49]
[null,null,"DC",{"$nulls":5},77.5,42.5]
[null,"200V","AC","50Hz",{"$nulls":4},135,97.5]
[null,null,null,"60Hz",200,240,160,"60~120",135,96]
[null,null,"DC",{"$nulls":5},150,81.5]
[null,"300V","AC","60Hz",265,347,212,"80~159",198,146]
[null,"400V","AC","60Hz",380,450,304,"114~228",264,170]
[null,"500V","AC","60Hz",440,575,352,"132~264",350,250]