{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":49,"n_cols":11,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["American Wire Gauge -- IEC 60228 Wire Size"]
[]
["AWG / kcmil","Area   Circ Mils","mm2","Amps   TW/UF (60C)","Amps THHW (75C)","Amps THHN (90C)",null,"IEC mm2","Area   Circ Mils","Amps Free Air, 70C PVC","Amps    in wall, 70C PVC"]
[18,1620,0.820854,"--","--",null,null,0.5,987,"  --","  --"]
[16,2580,1.307286,"--","--",null,null,0.75,1480.5,"--","--"]
["14*",4110,2.082537,"20 (15)","20 (15)","25 (20)",null,1.5,2961,17.5,13]
["12*",6530,3.308751,"25 (20)","25 (20)","30 (20)",null,2.5,4935,24,17.5]
["10*",10380,5.259546,30,"35 (30)","40 (30)",null,4,7896,32,23]
[8,16510,8.365617,40,50,55,null,6,11844,41,29]
[6,26240,13.295808000000001,55,65,75,null,10,19740,57,39]
[4,41740,21.149658,70,85,95,null,16,31584,76,52]
[3,52620,26.662554,85,100,110,null,25,49350,96,68]
[2,66360,33.624612,95,115,130,null,35,69090,119,83]
[1,83690,42.405723,110,130,150,null,50,98700,144,99]
["1/0",105600,53.50752,125,150,170,null,70,138180,184,125]
["2/0",133100,67.44177,145,175,195,null,95,187530,223,150]
["3/0",167800,85.02426,165,200,225,null,120,236880,259,172]
["4/0",211600,107.21772,195,230,260,null,150,296100,299,196]
["250",250000,126.675,215,255,290,null,185,365190,341,223]
["300",300000,152.01,240,285,320,null,240,473760,403,261]
["350",350000,177.345,260,310,350,null,300,592200,464,298]
["400",400000,202.68,280,335,380]
["500",500000,253.35,320,380,430,null,"(table A.52.4 of IEC 60364-5-52)"]
["600",600000,304.02,355,420,475,null,"Fig. G20, http://tinyurl.com/2u3pzqd"]
["700",700000,354.69,385,460,520]
["750",750000,380.02500000000003,400,475,535]
["800",800000,405.36,410,490,555]
["900",900000,456.03000000000003,435,520,585]
["1000",1000000,506.7,455,545,615]
[]
["   * Maximum overcurrent protection for # 14 = 15A, # 12 = 20A, # 10 = 30A"]
[]
[null,"NEC 2007, Chap 9, Table 8, via Ugly's Electrical Ref 2008, pp71, 73"]
[]
["Short-time Withstand Rating"]
["Copper conductors and bolted connections withstand rating: (NEC 250-94, 250-95)"]
["1 Ampere for 5 seconds per: "]
["30 circular mils (bare wire)"]
["42.25 circular mils (75°C insulated wire)"]
[]
["Conversions"]
["kcmil = Square Inches x 1273"]
["kcmil = Square Millimeters x 1.974"]
["mm2 = kcmil x 0.5067"]
[]
[null,"2007 Erico Cadweld Catalog, Technical Information (page B-4)"]
[]
[]
["https://www.metatek.org/reference/awg-iec-wire"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}